## Pipe Expansion
PIPE THERMAL EXPANSION
Data
Pipe Material
Diameter of pipe DN |  | in
Schedule SCH
Pipe Outer diameter OD | 88.9 | mm
Thickness | 5.49 | mm
Pipe Inner diameter ID | 77.92 | mm
Linst | 10 | m
tinst Minimum temperature | 20 | ºC
toperation Maximum temperature | 300 | °C
ΔT Differential temperature | 280 | ºC
Allowable stress σallow | 122.3682 | N/mm2
Linear expansion coefficient l | 1.4415e-05 | m/(m*ºC)
Elasticity module E | 185271.9783 | N/mm2
Tension σ | 747.8141 | N/mm2 | σ = E * DL/Linst
Section S | 4768.5656 | mm2
Results
Equivalent force F | 3566000.7435 | N | F = σ * S
Linear expansion of pipe DL | 0.040363 | m | DL= l * Linst * ΔT
Input values for calculation
Spreadsheet calculation
Final result
| Annexes A, B y C | [12 empty] | 10 | 30 | 40 | 80
| Anexo A | [7 empty] | Se asume que el punto "A" corresponde |  | 1 | 0.5 | 21.3 | 2.11 | 2.41 | 2.77 | 3.73 | 8
| Interpolación para el esfuerzo admisible del material |  |  |  |  | (Tabla A-1, Hoja 3) |  |  | al caso de una viga empotrada en cuyo |  | 2 | 0.75 | 26.7 | 2.11 | 2.41 | 2.87 | 3.91 | 3
[9 empty] | extremo "C" se produce una deflección |  | 3 | 1 | 33.4 | 2.77 | 2.9 | 3.38 | 4.55
| t = | 300 | °C | (Para t < 38 °C, la tabla utiliza 38 °C) |  |  |  |  | DL/2. Para deflexión máxima de la viga, |  | 4 | 1.25 | 42.2 | 2.77 | 2.97 | 3.56 | 4.85
| Row = | 5 | (Selected material) | [5 empty] | se quiere que ésta no sufra un esfuerzo |  | 5 | 1.5 | 48.3 | 2.77 | 3.18 | 3.68 | 5.08
[9 empty] | superior a sallow. |  | 6 | 2 | 60.3 | 2.77 | 3.18 | 3.91 | 5.54
| Col_A = | 7 | tA = | 260 | °C | sA = | 130.311 | MPa |  |  | 7 | 2.5 | 73 | 3.05 | 4.78 | 5.16 | 7.01
| Col_B = | 8 | tB = | 315.5556 | °C | sB = | 119.2793 | MPa | Tipo de lira |  | 8 | 3 | 88.9 | 3.05 | 4.78 | 5.49 | 7.62
[9 empty] | L = | 2 * W | 9 | 4 | 114.3 | 3.05 | 4.78 | 6.02 | 8.56
| S = | sB + (sA - sB) * (tb - t)/(tb - ta) | [8 empty] | 10 | 5 | 141.3 | 3.4 | 5.56 | 6.55 | 9.53
| S = | 122.3682 | MPa | TRUE | [6 empty] | 11 | 6 | 168.3 | 3.4 | 6.35 | 7.11 | 10.97
[11 empty] | 12 | 8 | 219.1 | 3.76 | 7.04 | 8.18 | 12.7
| Anexo B | [9 empty] | 13 | 10 | 273 | 4.19 | 7.8 | 9.27 | 15.09
| Interpolación para el módulo de elasticidad del tipo de material |  |  |  |  | (Tabla B, Hoja 5) |  |  |  |  | 14 | 12 | 323.8 | 4.57 | 8.38 | 10.31 | 17.48
|  |  |  | Para t < -200 °C, se usan datos para -200 °C | [6 empty] | 15 | 14 | 355.6 | 6.35 | 9.53 | 11.13 | 19.05
| t = | 300 | °C | Información disponible, para la mayoría de los tipos de materiales, tmax = 649 °C. | [6 empty] | 16 | 16 | 406.4 | 6.35 | 9.53 | 12.7 | 21.44
| Row = | 1 | (Selected material) | [5 empty] | TRUE |  | 17 | 18 | 457 | 6.35 | 11.13 | 14.27 | 23.83
[8 empty] | MPa | TRUE |  | 18 | 20 | 508 | 6.35 | 12.7 | 15.09 | 26.19
| Col_A = | 9 | tA = | 260 | °C | EA = | 188226874290 |  | TRUE
| Col_B = | 10 | tB = | 316 | °C | EB = | 184090019910 | MPa
| E = | EB + (EA - EB) * (tb - t)/(tb - ta)
| E = | 185271.9783 | MPa | TRUE
10
| Anexo C | [16 empty] | 30
| Interpolación para el coeficiente de expansión térmica del material |  |  |  |  | (Tabla C, Hoja 4) | [11 empty] | 40
80
| t = | 300 | °C | (Para t < 38 °C, la tabla utiliza 38 °C)
| Row = | 1 | (Selected material)
| Col_A = | 62 | tA = | 297.7778 | °C | lA = | 1.4403e-05 | m/(m*K)
| Col_B = | 63 | tB = | 311.6667 | °C | lB = | 1.448e-05 | m/(m*K)
| l = | sB + (sA - sB) * (tb - t)/(tb - ta)
| l = | 1.4415e-05 | m/(m*C) | TRUE
Do not delete these lines

## Linear Expansion
Table C-1
Thermal expansion coefficient " l " [m/(m*C)] for metals
| 1 | Temperatura °C
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80
| Material | -535.5556 | -521.6667 | -507.7778 | -493.8889 | -480 | -466.1111 | -452.2222 | -438.3333 | -424.4444 | -410.5556 | -396.6667 | -382.7778 | -368.8889 | -355 | -341.1111 | -327.2222 | -313.3333 | -299.4444 | -285.5556 | -271.6667 | -257.7778 | -246.6667 | -230 | -216.1111 | -202.2222 | -188.3333 | -174.4444 | -160.5556 | -146.6667 | -132.7778 | -118.8889 | -105 | -91.1111 | -77.2222 | -63.3333 | -49.4444 | -35.5556 | -21.6667 | -7.7778 | 6.1111 | 20 | 33.8889 | 47.7778 | 61.6667 | 75.5556 | 89.4444 | 103.3333 | 117.2222 | 131.1111 | 145 | 158.8889 | 172.7778 | 186.6667 | 200.5556 | 214.4444 | 228.3333 | 242.2222 | 256.1111 | 270 | 283.8889 | 297.7778 | 311.6667 | 325.5556 | 339.4444 | 353.3333 | 367.2222 | 381.1111 | 395 | 408.8889 | 422.7778 | 436.6667 | 450.5556 | 464.4444 | 478.3333 | 492.2222 | 506.1111 | 520 | 533.8889 | 547.7778
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80
1 | Carbon Steel Carbon-Moly- Low-Chrome (Through 3Cr-Mo) | 0 | 0 | 0 | 0 | 0 | 9e-06 | 9.0811e-06 | 9.1739e-06 | 9.2813e-06 | 9.4068e-06 | 9.5e-06 | 9.6735e-06 | 9.8864e-06 | 1e-05 | 1.0147e-05 | 1.0345e-05 | 1.05e-05 | 1.0737e-05 | 1.05e-05 | 1.0667e-05 | 1.05e-05 | 1.09e-05 | 1.15e-05 | 1.1455e-05 | 1.1438e-05 | 1.1429e-05 | 1.1423e-05 | 1.171e-05 | 1.1667e-05 | 1.178e-05 | 1.187e-05 | 1.2e-05 | 1.2107e-05 | 1.2197e-05 | 1.2273e-05 | 1.238e-05 | 1.2474e-05 | 1.2556e-05 | 1.2628e-05 | 1.2725e-05 | 1.2844e-05 | 1.2921e-05 | 1.3019e-05 | 1.3135e-05 | 1.3216e-05 | 1.3314e-05 | 1.3405e-05 | 1.3511e-05 | 1.3588e-05 | 1.3681e-05 | 1.3767e-05 | 1.3848e-05 | 1.3942e-05 | 1.4031e-05 | 1.4114e-05 | 1.4175e-05 | 1.4233e-05 | 1.4287e-05 | 1.4339e-05 | 1.4403e-05 | 1.448e-05 | 1.4552e-05 | 1.4621e-05 | 1.4659e-05 | 1.4681e-05 | 1.4701e-05 | 1.4735e-05 | 1.4779e-05 | 1.4822e-05 | 1.4863e-05 | 1.4902e-05 | 1.494e-05 | 1.4977e-05 | 1.5011e-05 | 1.5045e-05 | 0 | 0 | 0 | 0
2 | 5Cr-Mo Through 9Cr-Mo | 0 | 0 | 0 | 0 | 0 | 8.4304e-06 | 8.5135e-06 | 8.6087e-06 | 8.7188e-06 | 8.8475e-06 | 9e-06 | 9.1837e-06 | 9.3409e-06 | 9.4615e-06 | 9.5294e-06 | 9.7241e-06 | 9.875e-06 | 9.9474e-06 | 9.8571e-06 | 1e-05 | 9.75e-06 | 1.025e-05 | 1.1e-05 | 1.0909e-05 | 1.0875e-05 | 1.0857e-05 | 1.0846e-05 | 1.0935e-05 | 1.1083e-05 | 1.1122e-05 | 1.1152e-05 | 1.1176e-05 | 1.125e-05 | 1.1311e-05 | 1.1364e-05 | 1.1493e-05 | 1.1566e-05 | 1.163e-05 | 1.1686e-05 | 1.1802e-05 | 1.1875e-05 | 1.1941e-05 | 1.2e-05 | 1.2081e-05 | 1.2129e-05 | 1.2198e-05 | 1.2238e-05 | 1.2321e-05 | 1.2397e-05 | 1.2468e-05 | 1.2534e-05 | 1.2596e-05 | 1.2673e-05 | 1.2727e-05 | 1.2777e-05 | 1.2825e-05 | 1.2886e-05 | 1.2945e-05 | 1.3e-05 | 1.3037e-05 | 1.3087e-05 | 1.3134e-05 | 1.318e-05 | 1.3194e-05 | 1.3222e-05 | 1.3249e-05 | 1.3274e-05 | 1.3325e-05 | 1.3386e-05 | 1.3432e-05 | 1.3488e-05 | 1.3506e-05 | 1.3535e-05 | 1.3563e-05 | 1.359e-05 | 0 | 0 | 0 | 0
3 | Austenitic Stainless Steels 18Cr-8Ni | 0 | 0 | 0 | 0 | 0 | 1.462e-05 | 1.4716e-05 | 1.4826e-05 | 1.4953e-05 | 1.5051e-05 | 1.5167e-05 | 1.5306e-05 | 1.5477e-05 | 1.5462e-05 | 1.5441e-05 | 1.5517e-05 | 1.55e-05 | 1.5474e-05 | 1.5429e-05 | 1.5333e-05 | 1.575e-05 | 1.625e-05 | 1.7e-05 | 1.6909e-05 | 1.6875e-05 | 1.6857e-05 | 1.6846e-05 | 1.6935e-05 | 1.6917e-05 | 1.6976e-05 | 1.7022e-05 | 1.7059e-05 | 1.7143e-05 | 1.7213e-05 | 1.7273e-05 | 1.7324e-05 | 1.7408e-05 | 1.7444e-05 | 1.7477e-05 | 1.7505e-05 | 1.7562e-05 | 1.7614e-05 | 1.766e-05 | 1.7703e-05 | 1.7767e-05 | 1.7802e-05 | 1.7857e-05 | 1.7908e-05 | 1.7978e-05 | 1.8021e-05 | 1.8082e-05 | 1.8139e-05 | 1.8192e-05 | 1.8242e-05 | 1.8289e-05 | 1.8351e-05 | 1.8409e-05 | 1.8464e-05 | 1.8516e-05 | 1.8565e-05 | 1.8612e-05 | 1.8657e-05 | 1.8699e-05 | 1.8739e-05 | 1.8778e-05 | 1.8814e-05 | 1.885e-05 | 1.8883e-05 | 1.8915e-05 | 1.8946e-05 | 1.8976e-05 | 1.9004e-05 | 1.9031e-05 | 1.9057e-05 | 1.9083e-05 | 1.9151e-05 | 1.9228e-05 | 1.9302e-05 | 1.9374e-05
4 | 12Cr, 17Cr, 27Cr | 0 | 0 | 0 | 0 | 0 | 7.7468e-06 | 7.7838e-06 | 7.8261e-06 | 7.875e-06 | 7.9831e-06 | 8.1111e-06 | 8.2653e-06 | 8.4545e-06 | 8.5385e-06 | 8.6471e-06 | 8.7931e-06 | 9e-06 | 9e-06 | 9e-06 | 9e-06 | 9e-06 | 9.4e-06 | 1e-05 | 9.8182e-06 | 9.9375e-06 | 9.8571e-06 | 9.9231e-06 | 9.9677e-06 | 1.0083e-05 | 1.0098e-05 | 1.0174e-05 | 1.0235e-05 | 1.0339e-05 | 1.0377e-05 | 1.0455e-05 | 1.0563e-05 | 1.0618e-05 | 1.0704e-05 | 1.0744e-05 | 1.0813e-05 | 1.0906e-05 | 1.096e-05 | 1.1038e-05 | 1.1081e-05 | 1.1147e-05 | 1.1207e-05 | 1.1262e-05 | 1.1313e-05 | 1.1382e-05 | 1.1447e-05 | 1.1507e-05 | 1.1563e-05 | 1.1635e-05 | 1.1683e-05 | 1.1729e-05 | 1.1772e-05 | 1.183e-05 | 1.1884e-05 | 1.1935e-05 | 1.1969e-05 | 1.2168e-05 | 1.2209e-05 | 1.2102e-05 | 1.2128e-05 | 1.2167e-05 | 1.219e-05 | 1.2212e-05 | 1.2234e-05 | 1.2267e-05 | 1.2299e-05 | 1.2329e-05 | 1.2347e-05 | 1.2375e-05 | 1.2391e-05 | 1.2417e-05 | 0 | 0 | 0 | 0
5 | 25Cr-20Ni | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6e-05 | 1.5818e-05 | 1.575e-05 | 1.5714e-05 | 1.5808e-05 | 1.5871e-05 | 1.5917e-05 | 1.5951e-05 | 1.5978e-05 | 1.6e-05 | 1.6018e-05 | 1.6033e-05 | 1.6045e-05 | 1.6056e-05 | 1.6066e-05 | 1.6074e-05 | 1.6081e-05 | 1.6088e-05 | 1.6094e-05 | 1.6099e-05 | 1.6104e-05 | 1.6108e-05 | 1.6112e-05 | 1.6116e-05 | 1.6119e-05 | 1.6122e-05 | 1.6125e-05 | 1.6128e-05 | 1.613e-05 | 1.6192e-05 | 1.625e-05 | 1.6304e-05 | 1.6355e-05 | 1.6404e-05 | 1.6449e-05 | 1.6492e-05 | 1.6532e-05 | 1.6571e-05 | 1.6607e-05 | 1.6642e-05 | 1.6675e-05 | 1.6749e-05 | 1.6819e-05 | 1.6887e-05 | 1.6951e-05 | 1.7013e-05 | 1.7072e-05 | 1.7129e-05 | 1.7183e-05 | 1.7199e-05 | 1.7215e-05 | 1.723e-05 | 1.7244e-05 | 0 | 0 | 0 | 0
6 | UNS N04400 Monel 67Ni-30Cu | 0 | 0 | 0 | 0 | 0 | 9.9494e-06 | 1.0135e-05 | 1.0348e-05 | 1.0594e-05 | 1.0881e-05 | 1.1222e-05 | 1.1633e-05 | 1.2205e-05 | 1.2231e-05 | 1.2176e-05 | 1.2207e-05 | 1.225e-05 | 1.2158e-05 | 1.2214e-05 | 1.2333e-05 | 1.5e-05 | 1.46e-05 | 1.4e-05 | 1.4182e-05 | 1.4062e-05 | 1.4143e-05 | 1.4077e-05 | 1.4129e-05 | 1.425e-05 | 1.4341e-05 | 1.4413e-05 | 1.4353e-05 | 1.4357e-05 | 1.4311e-05 | 1.4773e-05 | 1.4873e-05 | 1.4961e-05 | 1.5037e-05 | 1.5105e-05 | 1.5198e-05 | 1.5312e-05 | 1.5386e-05 | 1.5453e-05 | 1.5541e-05 | 1.5647e-05 | 1.5719e-05 | 1.581e-05 | 1.5893e-05 | 1.5993e-05 | 1.6064e-05 | 1.613e-05 | 1.6212e-05 | 1.6308e-05 | 1.6398e-05 | 1.6482e-05 | 1.6561e-05 | 1.6653e-05 | 1.6724e-05 | 1.6806e-05 | 1.6885e-05 | 1.6974e-05 | 1.706e-05 | 1.7141e-05 | 1.7218e-05 | 1.7319e-05 | 1.7389e-05 | 1.7456e-05 | 1.7532e-05 | 1.7619e-05 | 1.7701e-05 | 1.778e-05 | 1.7857e-05 | 1.793e-05 | 1.8e-05 | 1.8068e-05 | 0 | 0 | 0 | 0
7 | 3.5Ni | 0 | 0 | 0 | 0 | 0 | 8.5443e-06 | 8.7973e-06 | 9e-06 | 9.1875e-06 | 9.4576e-06 | 9.7778e-06 | 9.9184e-06 | 1.0091e-05 | 1.0231e-05 | 1.0324e-05 | 1.0448e-05 | 1.05e-05 | 1.0579e-05 | 1.0714e-05 | 1.0667e-05 | 1.125e-05 | 1.135e-05 | 1.15e-05 | 1.1455e-05 | 1.1438e-05 | 1.1571e-05 | 1.1654e-05 | 1.171e-05 | 1.1833e-05 | 1.1927e-05 | 1.2e-05 | 1.2059e-05 | 1.2107e-05 | 1.2148e-05 | 1.2227e-05 | 1.2296e-05 | 1.2355e-05 | 1.2407e-05 | 1.2488e-05 | 1.256e-05 | 1.2625e-05 | 1.2683e-05 | 1.2736e-05 | 1.2811e-05 | 1.2879e-05 | 1.2942e-05 | 1.3e-05 | 1.3053e-05 | 1.3103e-05 | 1.3149e-05 | 1.3212e-05 | 1.3272e-05 | 1.3327e-05 | 1.3379e-05 | 1.3428e-05 | 1.3474e-05 | 1.3517e-05 | 1.3541e-05 | 1.3565e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | Copper and Copper Alloys | 1.1337e-05 | 1.1909e-05 | 1.2479e-05 | 1.3045e-05 | 1.3536e-05 | 1.3937e-05 | 1.4311e-05 | 1.4609e-05 | 1.4859e-05 | 1.5102e-05 | 1.5333e-05 | 1.549e-05 | 1.5682e-05 | 1.5846e-05 | 1.5971e-05 | 1.6138e-05 | 1.625e-05 | 1.6421e-05 | 1.65e-05 | 1.6667e-05 | 1.65e-05 | 1.67e-05 | 1.7e-05 | 1.7182e-05 | 1.7063e-05 | 1.7143e-05 | 1.7192e-05 | 1.7323e-05 | 1.7417e-05 | 1.7415e-05 | 1.7478e-05 | 1.7588e-05 | 1.7625e-05 | 1.7656e-05 | 1.7727e-05 | 1.7789e-05 | 1.7803e-05 | 1.7852e-05 | 1.793e-05 | 1.7967e-05 | 1.8e-05 | 1.803e-05 | 1.7236e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | Aluminum | 0 | 0 | 0 | 0 | 0 | 1.7772e-05 | 1.8081e-05 | 1.8304e-05 | 1.8609e-05 | 1.8864e-05 | 1.9111e-05 | 1.9347e-05 | 1.9636e-05 | 1.9769e-05 | 2.0029e-05 | 2.0379e-05 | 2.0875e-05 | 2.0842e-05 | 2.0786e-05 | 2.1e-05 | 2.1e-05 | 2.18e-05 | 2.3e-05 | 2.3182e-05 | 2.3063e-05 | 2.3143e-05 | 2.3077e-05 | 2.3323e-05 | 2.3583e-05 | 2.3707e-05 | 2.3935e-05 | 2.4059e-05 | 2.4214e-05 | 2.4344e-05 | 2.45e-05 | 2.4634e-05 | 2.4789e-05 | 2.4889e-05 | 2.5012e-05 | 2.5154e-05 | 2.5312e-05 | 2.5426e-05 | 2.5557e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | Gray Cast Iron | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05e-05 | 1.0364e-05 | 1.0312e-05 | 1.0429e-05 | 1.0385e-05 | 1.0452e-05 | 1.0583e-05 | 1.061e-05 | 1.0696e-05 | 1.0765e-05 | 1.0875e-05 | 1.0918e-05 | 1.1e-05 | 1.107e-05 | 1.1171e-05 | 1.1222e-05 | 1.1302e-05 | 1.1407e-05 | 1.1469e-05 | 1.1554e-05 | 1.1632e-05 | 1.173e-05 | 1.1819e-05 | 1.1901e-05 | 1.1976e-05 | 1.2046e-05 | 1.2132e-05 | 1.2213e-05 | 1.2288e-05 | 1.2358e-05 | 1.2442e-05 | 1.2522e-05 | 1.2596e-05 | 1.2684e-05 | 1.2784e-05 | 1.2862e-05 | 1.2935e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | Bronze | 0 | 0 | 0 | 0 | 0 | 1.5114e-05 | 1.5162e-05 | 1.5217e-05 | 1.5281e-05 | 1.5356e-05 | 1.5444e-05 | 1.5551e-05 | 1.575e-05 | 1.5846e-05 | 1.5971e-05 | 1.6138e-05 | 1.65e-05 | 1.9737e-05 | 1.65e-05 | 1.6333e-05 | 1.65e-05 | 1.71e-05 | 1.8e-05 | 1.8e-05 | 1.8e-05 | 1.8e-05 | 1.8e-05 | 1.8e-05 | 1.8083e-05 | 1.8146e-05 | 1.8196e-05 | 1.8294e-05 | 1.8321e-05 | 1.8393e-05 | 1.8409e-05 | 1.8465e-05 | 1.8513e-05 | 1.8556e-05 | 1.8593e-05 | 1.8626e-05 | 1.8688e-05 | 1.8743e-05 | 1.8792e-05 | 1.8811e-05 | 1.8853e-05 | 1.8893e-05 | 1.8929e-05 | 1.8962e-05 | 1.9015e-05 | 1.9064e-05 | 1.911e-05 | 1.9152e-05 | 1.9212e-05 | 1.9248e-05 | 1.9301e-05 | 1.9333e-05 | 1.9381e-05 | 1.9409e-05 | 1.9435e-05 | 1.9476e-05 | 1.9531e-05 | 1.9567e-05 | 1.9617e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | Brass | 0 | 0 | 0 | 0 | 0 | 1.4734e-05 | 1.4757e-05 | 1.4783e-05 | 1.4812e-05 | 1.4898e-05 | 1.5e-05 | 1.5122e-05 | 1.5273e-05 | 1.5385e-05 | 1.5529e-05 | 1.5724e-05 | 1.6125e-05 | 1.6105e-05 | 1.6071e-05 | 1.6e-05 | 1.575e-05 | 1.645e-05 | 1.75e-05 | 1.7455e-05 | 1.7625e-05 | 1.7571e-05 | 1.7538e-05 | 1.771e-05 | 1.7833e-05 | 1.7927e-05 | 1.8e-05 | 1.8118e-05 | 1.8268e-05 | 1.8344e-05 | 1.8409e-05 | 1.8507e-05 | 1.8632e-05 | 1.8741e-05 | 1.8837e-05 | 1.8956e-05 | 1.9062e-05 | 1.9158e-05 | 1.9245e-05 | 1.9351e-05 | 1.9474e-05 | 1.9562e-05 | 1.9667e-05 | 1.9786e-05 | 1.9897e-05 | 2e-05 | 2.0096e-05 | 2.0205e-05 | 2.0327e-05 | 2.0422e-05 | 2.0512e-05 | 2.0614e-05 | 2.0727e-05 | 2.0834e-05 | 2.0935e-05 | 2.1031e-05 | 2.1138e-05 | 2.1239e-05 | 2.1335e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | 70Cu-30Ni | 0 | 0 | 0 | 0 | 0 | 1.1962e-05 | 1.1635e-05 | 1.1739e-05 | 1.1859e-05 | 1.2e-05 | 1.2167e-05 | 1.298e-05 | 1.3295e-05 | 1.3385e-05 | 1.35e-05 | 1.3759e-05 | 1.4125e-05 | 1.4053e-05 | 1.4143e-05 | 1.4e-05 | 1.425e-05 | 1.475e-05 | 1.55e-05 | 1.5273e-05 | 1.5375e-05 | 1.5286e-05 | 1.5346e-05 | 1.5387e-05 | 1.55e-05 | 1.5585e-05 | 1.5652e-05 | 1.5765e-05 | 1.5857e-05 | 1.5934e-05 | 1.6e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | UNS N08XXX Series Ni-Fe-Cr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4e-05 | 1.4182e-05 | 1.425e-05 | 1.4143e-05 | 1.4192e-05 | 1.4419e-05 | 1.4667e-05 | 1.4854e-05 | 1.5e-05 | 1.5235e-05 | 1.5429e-05 | 1.5639e-05 | 1.5818e-05 | 1.5887e-05 | 1.5947e-05 | 1.5963e-05 | 1.6012e-05 | 1.6055e-05 | 1.6125e-05 | 1.6158e-05 | 1.6189e-05 | 1.6243e-05 | 1.6293e-05 | 1.6314e-05 | 1.6381e-05 | 1.642e-05 | 1.6478e-05 | 1.6511e-05 | 1.6562e-05 | 1.6589e-05 | 1.6654e-05 | 1.6677e-05 | 1.6735e-05 | 1.6772e-05 | 1.6824e-05 | 1.6873e-05 | 1.6919e-05 | 1.6963e-05 | 1.7005e-05 | 1.7045e-05 | 1.7097e-05 | 1.7133e-05 | 1.7194e-05 | 1.7226e-05 | 1.7283e-05 | 1.7351e-05 | 1.7428e-05 | 1.7477e-05 | 1.7549e-05 | 1.7618e-05 | 1.7695e-05 | 1.7747e-05 | 1.782e-05 | 1.7889e-05 | 1.7967e-05 | 1.8021e-05 | 1.8094e-05
15 | UNS N06XXX Series Ni-Cr-Fe | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3e-05 | 1.3091e-05 | 1.3125e-05 | 1.3143e-05 | 1.3269e-05 | 1.3355e-05 | 1.3417e-05 | 1.3537e-05 | 1.363e-05 | 1.3647e-05 | 1.3714e-05 | 1.377e-05 | 1.3864e-05 | 1.3901e-05 | 1.3934e-05 | 1.4e-05 | 1.4023e-05 | 1.4077e-05 | 1.4125e-05 | 1.4168e-05 | 1.4208e-05 | 1.4243e-05 | 1.4302e-05 | 1.4355e-05 | 1.4405e-05 | 1.445e-05 | 1.4493e-05 | 1.4553e-05 | 1.4589e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | Ductile Iron | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3889e-06 | 8.6327e-06 | 8.7955e-06 | 8.9231e-06 | 9.1765e-06 | 9.4138e-06 | 9.625e-06 | 9.7895e-06 | 9.8571e-06 | 7.6667e-06 | 1.05e-05 | 1.05e-05 | 1.05e-05 | 1.0636e-05 | 1.0688e-05 | 1.0857e-05 | 1.0846e-05 | 1.0935e-05 | 1.1083e-05 | 1.1195e-05 | 1.1217e-05 | 1.1353e-05 | 1.1411e-05 | 1.1607e-05 | 1.1636e-05 | 1.1789e-05 | 1.2e-05 | 1.2148e-05 | 1.2349e-05 | 1.2396e-05 | 1.2469e-05 | 1.2535e-05 | 1.2566e-05 | 1.2595e-05 | 1.2672e-05 | 1.2744e-05 | 1.2833e-05 | 1.2824e-05 | 1.2904e-05 | 1.2979e-05 | 1.3048e-05 | 1.3093e-05 | 1.3173e-05 | 1.3211e-05 | 1.3283e-05 | 1.3404e-05 | 1.3398e-05 | 1.3442e-05 | 1.3468e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## 6.CS_Imp (hidden)
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
2
3 | Pipe Thickness [mm], according ASME B36.10M
4
5 | [6 empty] | ASME B36.10M SCHEDULE / IDENTIFICATION | [9 empty] | Application |  | Dn = | 10 | in
6 | Size | dext | 5 | 10 | 20 | 30 | 40 | 60 | 80 | 100 | 120 | 140 | 160 | STD | XS | XXS | (with input validation) |  | SCH = | XXS | -
7 | 0.5 | 21.3 | 1.65 | 2.11 | - | 2.41 | 2.77 | - | 3.73 | - | 0 | - | 4.78 | 2.77 | 3.73 | 7.47 | di = | Pipe_Imp_CS_Dint_dn_sch |  | #NAME? | mm
8 | 0.75 | 26.7 | 1.65 | 2.11 | - | 2.41 | 2.87 | - | 3.91 | - | 0 | - | 5.56 | 2.87 | 3.91 | 7.82 | de = | Pipe_Imp_CS_Dext_dn |  | #NAME? | mm
9 | 1 | 33.4 | 1.65 | 2.77 | - | 2.9 | 3.38 | - | 4.55 | - | 0 | - | 6.35 | 3.38 | 4.55 | 9.09 | s = | Pipe_Imp_CS_Thickness_dn_sch |  | #NAME? | mm
10 | 1.25 | 42.2 | 1.65 | 2.77 |  | 2.97 | 3.56 |  | 4.85 |  |  |  | 6.35 | 3.56 | 4.85 | 9.7
11 | 1.5 | 48.3 | 1.65 | 2.77 | - | 3.18 | 3.68 | - | 5.08 | - | 0 | - | 7.14 | 3.68 | 5.08 | 10.15
12 | 2 | 60.3 | 1.65 | 2.77 | - | 3.18 | 3.91 | - | 5.54 | - | 0 | - | 8.74 | 3.91 | 5.54 | 11.07 | Application |  | Dn = | 16 | in
13 | 2.5 | 73 | 2.11 | 3.05 |  | 4.78 | 5.16 |  | 7.01 |  |  |  | 9.53 | 5.16 | 7.01 | 14.02
14 | 3 | 88.9 | 2.11 | 3.05 | - | 4.78 | 5.49 | - | 7.62 | - | 0 | - | 11.13 | 5.49 | 7.62 | 15.24 | (without input validation) |  | SCH = | 81
15 | 3.5 | 101.6 | 2.11 | 3.05 |  | 4.78 | 5.74 |  | 8.08 |  |  |  |  | 5.74 | 8.08
16 | 4 | 114.3 | 2.11 | 3.05 | - | 4.78 | 6.02 | - | 8.56 | - | 11.13 | - | 13.49 | 6.02 | 8.56 | 17.12 | di = | Pipe_Imp_CS_Dint_dn_sch |  | N/A | mm
17 | 5 | 141.3 | 2.77 | 3.4 | - | - | 6.55 | - | 9.53 | - | 12.7 | - | 15.88 | 6.55 | 9.53 | 19.05 | de = | Pipe_Imp_CS_Dext_dn |  | 559 | mm
18 | 6 | 168.3 | 2.77 | 3.4 | - | - | 7.11 | - | 10.97 | - | 14.27 | - | 18.26 | 7.11 | 10.97 | 21.95 | s = | Pipe_Imp_CS_Thickness_dn_sch |  | N/A | mm
19 | 8 | 219.1 | 2.77 | 3.76 | 6.35 | 7.04 | 8.18 | 10.31 | 12.7 | 15.09 | 18.26 | 20.62 | 23.01 | 8.18 | 12.7 | 22.23 | The shedule entered is wrong
20 | 10 | 273 | 3.4 | 4.19 | 6.35 | 7.8 | 9.27 | 12.7 | 15.09 | 18.26 | 21.44 | 25.4 | 28.58 | 9.27 | 12.7 | 25.4
21 | 12 | 323.8 | 3.96 | 4.57 | 6.35 | 8.38 | 10.31 | 14.27 | 17.48 | 21.44 | 25.4 | 28.58 | 33.32 | 9.53 | 12.7 | 25.4
22 | 14 | 355.6 | 3.96 | 6.35 | 7.92 | 9.53 | 11.13 | 15.09 | 19.05 | 23.83 | 27.79 | 31.75 | 35.71 | 9.53 | 12.7 | -
23 | 16 | 406.4 | 4.19 | 6.35 | 7.92 | 9.53 | 12.7 | 16.66 | 21.44 | 26.19 | 30.96 | 36.53 | 40.49 | 9.53 | 12.7 | -
24 | 18 | 457 | 4.19 | 6.35 | 7.92 | 11.13 | 14.27 | 19.05 | 23.83 | 29.36 | 34.93 | 39.67 | 45.24 | 9.53 | 12.7 | -
25 | 20 | 508 | 4.78 | 6.35 | 9.53 | 12.7 | 15.09 | 20.62 | 26.19 | 32.54 | 38.1 | 44.45 | 50.01 | 9.53 | 12.7 | -
26 | 22 | 559 | 4.78 | 6.35 | 9.53 | 12.7 | - | 22.23 | 28.58 | 34.93 | 41.28 | 47.63 | 53.98 | 9.53 | 12.7 | -
27 | 24 | 610 | 5.54 | 6.35 | 9.53 | 14.27 | 17.48 | 24.61 | 30.96 | 38.89 | 46.02 | 52.37 | 59.54 | 9.53 | 12.7 | -
28 | 26 | 660 | - | 7.92 | 12.7 | 15.88 | - | - | - | - | - | - | - | 9.53 | 12.7 | -
29 | 28 | 711 | - | 7.92 | 12.7 | - | - | - | - | - | - | - | - | 9.53 | 12.7 | -
30 | 30 | 762 | 6.35 | 7.92 | 12.7 | 15.88 | - | - | - | - | - | - | - | 9.53 | 12.7 | -
31 | 32 | 813 | - | 7.92 | 12.7 | 15.88 | 17.48 | - | - | - | - | - | - | 9.53 | 12.7 | -
32 | 34 | 864 | - | 7.92 | 12.7 | 15.88 | 17.48 | - | - | - | - | - | - | 9.53 | 12.7 | -
33 | 36 | 914 | - | 7.92 | 12.7 | 15.88 | 19.05 | - | - | - | - | - | - | 9.53 | 12.7 | -
34 | 38 | 965 | - | - | - | - | - | - | - | - | - | - | - | 9.53 | 12.7 | -
35 | 40 | 1016 | - | - | - | - | - | - | - | - | - | - | - | 9.53 | 12.7 | -
36 | 42 | 1067 | - | - | - | - | - | - | - | - | - | - | - | 9.53 | 12.7 | -
| 44 | 1118 | - | - | - | - | - | - | - | - | - | - | - | 9.53 | 12.7 | -
| 46 | 1168 | - | - | - | - | - | - | - | - | - | - | - | 9.53 | 12.7 | -
39 | 48 | 1219 | - | - | - | - | - | - | - | - | - | - | - | 9.53 | 12.7 | -
Carbon steel pipes
| dn | Sc -
in
| 0.5 | 5
| 0.75 | 10
| 1 | 20
| 1.5 | 30
| 2 | 40
| 3 | 60
| 4 | 80
| 5 | 100
| 6 | 120
| 8 | 140
| 10 | 160
| 12 | STD
| 14 | XS
| 16 | XXS |  |  | Carbon steel pipes.
| 18 |  |  |  | dn: 1/2,3/4,1,1 1/2,2,3,4,5,6,8,10,12,14,16,18,20,22,24,26,28,30,32,34,36,38,40,42,44,46,48. Sch:5,10,20,30,40,60,80,100,120,140,160,STD,XS,XXS
20
22
24
26
28
30
32
34
36
38
40
42
44
46
48

## Allowable stress
| 5 |  | Allowable stress as function of temperature [MPa]
TEMPERATURE °C
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26
| Spec & Grade | Material | 37.7778 | 93.3333 | 148.8889 | 204.4444 | 260 | 315.5556 | 343.3333 | 371.1111 | 398.8889 | 426.6667 | 454.4444 | 482.2222 | 510 | 537.7778 | 565.5556 | 593.3333 | 621.1111 | 648.8889 | 676.6667 | 704.4444 | 732.2222 | 760 | 787.7778 | 815.5556
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26
1 | A 53(Type F) Gr.A |  | 110.3162 | 110.3162 | 110.3162 | 110.3162 | "N/A" | "N/A" | "N/A" | "N/A" | "N/A" | "N/A" | "N/A" | "N/A" | "N/A" | "N/A" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | "N/A" | 1 | 1
2 | A 53 - Gr. A |  | 110.3162 | 110.3162 | 110.3162 | 110.3162 | 110.3162 | 102.0424 | 99.974 | 99.2845 | 73.7739 | 64.1213 | 54.4686 | 44.8159 | 31.0264 | 17.2369 | 11.0316 | 6.8948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | "N/A" | 1 | 1
3 | A 53 - Gr. B |  | 137.8952 | 137.8952 | 137.8952 | 137.8952 | 130.311 | 119.2793 | 117.2109 | 113.7635 | 89.6319 | 74.4634 | 59.9844 | 44.8159 | 31.0264 | 17.2369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | "N/A" | 1 | 1
4 | A 106 - Gr. A |  | 110.3162 | 110.3162 | 110.3162 | 110.3162 | 110.3162 | 102.0424 | 99.974 | 99.2845 | 73.7739 | 64.1213 | 54.4686 | 44.8159 | 31.0264 | 17.2369 | 11.0316 | 6.8948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | "N/A" | 1 | 1
5 | A106 - Gr. B |  | 137.8952 | 137.8952 | 137.8952 | 137.8952 | 130.311 | 119.2793 | 117.2109 | 113.7635 | 89.6319 | 74.4634 | 59.9844 | 44.8159 | 31.0264 | 17.2369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | "N/A" | 1 | 1
6 | A106 - Gr. C |  | 160.6479 | 160.6479 | 160.6479 | 157.89 | 148.9268 | 135.8268 | 133.7583 | 132.3794 | 102.0424 | 82.7371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | "N/A" | 1 | 1
7 | API 5L - Gr. A |  | 110.3162 | 110.3162 | 110.3162 | 110.3162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | "N/A" | 1 | 1
8 | API 5L - Gr. A25 |  | 103.4214 | 103.4214 | 99.974 | 95.1477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | "N/A" | 1 | 1
9 | API 5L - Gr. B |  | 137.8952 | 137.8952 | 137.8952 | 137.8952 | 130.311 | 119.2793 | 117.2109 | 113.7635 | 89.6319 | 74.4634 | 59.9844 | 44.8159 | 31.0264 | 17.2369 | 11.0316 | 6.8948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | "N/A" | 1 | 1
10 | API 5L - Gr. X42 |  | 137.8952 | 137.8952 | 137.8952 | 137.8952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | "N/A" | 1 | 1
11 | API 5L - Gr. X46 |  | 144.79 | 144.79 | 144.79 | 144.79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
12 | API 5L - Gr. X52 |  | 151.6847 | 151.6847 | 151.6847 | 151.6847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
13 | API 5L - Gr. X56 |  | 163.4058 | 163.4058 | 163.4058 | 163.4058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
14 | API 5L - Gr. X60 |  | 172.369 | 172.4 | 172.369 | 172.369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
15 | API 5L - Gr. X65 |  | 177.1953 | 177.1953 | 177.1953 | 177.1953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
16 | API 5L - Gr. X70 |  | 188.2269 | 188.2269 | 188.2269 | 188.2269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
17 | API 5L - Gr. X80 |  | 206.8428 | 206.8428 | 206.8428 | 206.8428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
18 | A312 - Gr. TP 304 |  | 137.8952 | 137.8952 | 137.8952 | 128.932 | 120.6583 | 113.0741 | 111.6951 | 110.3162 | 107.5583 | 104.8004 | 102.7319 | 100.6635 | 99.2845 | 95.1477 | 84.1161 | 66.8792 | 53.0897 | 41.3686 | 32.4054 | 25.5106 | 19.9948 | 15.8579 | 12.4106 | 9.6527 | 3 | 9
19 | A312 - Gr. TP 304L |  | 115.1425 | 115.1425 | 115.1425 | 108.9372 | 102.0424 | 96.5266 | 94.4582 | 93.0793 | 91.7003 | 89.6319 | 88.2529 | 82.0476 | 68.2581 | 53.7791 | 43.437 | 35.1633 | 27.579 | 22.0632 | 17.9264 | 14.479 | 11.7211 | 7.5842 | 6.8948 | 6.2053 | 3 | 9
20 | A312 - Gr. TP 304H |  | 137.8952 | 137.8952 | 137.8952 | 128.932 | 120.6583 | 113.0741 | 111.6951 | 110.3162 | 107.5583 | 104.8004 | 102.7319 | 100.6635 | 99.2845 | 95.1477 | 84.1161 | 66.8792 | 53.0897 | 41.3686 | 32.4054 | 25.5106 | 19.9948 | 15.8579 | 12.4106 | 9.6527 | 3 | 9
21 | A312 - Gr. TP 309 |  | 137.8952 | 137.8952 | 137.8952 | 137.8952 | 137.8952 | 132.3794 | 129.6215 | 126.1741 | 124.1057 | 120.6583 | 100.6635 | 95.8372 | 86.1845 | 72.395 | 58.6055 | 44.8159 | 34.4738 | 26.2001 | 19.9948 | 15.8579 | 12.4106 | 8.9632 | 6.2053 | 4.8263 | 3 | 9
22 | A312 - Gr. TP 310 |  | 137.8952 | 137.8952 | 137.8952 | 137.8952 | 137.8952 | 132.3794 | 129.6215 | 126.1741 | 124.1057 | 120.6583 | 100.6635 | 95.8372 | 86.1845 | 75.8424 | 48.9528 | 34.4738 | 24.8211 | 17.2369 | 10.3421 | 5.5158 | 3.4474 | 2.7579 | 2.0684 | 1.379 | 5 | 9
23 | A312 - Gr. TP 316 |  | 137.8952 | 137.8952 | 137.8952 | 133.0689 | 123.4162 | 117.2109 | 115.1425 | 112.3846 | 111.0056 | 109.6267 | 108.2477 | 106.8688 | 106.1793 | 105.4898 | 99.974 | 85.495 | 67.5686 | 51.0212 | 37.9212 | 28.2685 | 21.3738 | 15.8579 | 11.7211 | 8.9632 | 4 | 9
24 | A312 - Gr. TP 316L |  | 115.1425 | 115.1425 | 115.1425 | 106.8688 | 99.2845 | 93.0793 | 91.0108 | 88.9424 | 86.874 | 85.495 | 83.4266 | 81.3582 | 79.2897 | 77.2213 | 74.4634 | 70.3266 | 60.6739 | 44.1265 | 32.4054 | 24.1317 | 17.2369 | 12.4106 | 8.9632 | 6.8948 | 4 | 9
25 | A312 - Gr. TP 316H |  | 137.8952 | 137.8952 | 137.8952 | 133.0689 | 123.4162 | 117.2109 | 115.1425 | 112.3846 | 111.0056 | 109.6267 | 108.2477 | 106.8688 | 106.1793 | 105.4898 | 99.974 | 85.495 | 67.5686 | 51.0212 | 37.9212 | 28.2685 | 21.3738 | 15.8579 | 11.7211 | 8.9632 | 4 | 9
26 | A312 - Gr. TP 317 |  | 137.8952 | 137.8952 | 137.8952 | 133.0689 | 123.4162 | 117.2109 | 115.1425 | 112.3846 | 111.0056 | 109.6267 | 108.2477 | 106.8688 | 106.1793 | 105.4898 | 99.974 | 85.495 | 67.5686 | 51.0212 | 37.9212 | 28.2685 | 21.3738 | 15.8579 | 11.7211 | 8.9632 | 4 | 9
27 | A312 - Gr. TP 317L |  | 137.8952 | 137.8952 | 137.8952 | 130.311 | 122.0373 | 115.832 | 114.453 | 111.6951 | 108.9372 | 106.8688 | 104.8004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 9
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26
[16 empty] | t = | 593 |  | 621
[16 empty] | S = | 66.9 |  | 53.1
[29 empty] | 1 | 1
1
2
3
4
5
6
7
8
9
10

## Elasticity modules
Table B. Young Modulus of Elasticity E [Pa]
| Metal | Temperature (oC) | [15 empty] | Metal | Temperature (oC)
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
| 1 | -200 | -129 | -73 | 21 | 93 | 149 | 204 | 260 | 316 | 371 | 427 | 482 | 538 | 593 | 649 |  |  | -200 | -129 | -73 | 21 | 93 | 149 | 204 | 260 | 316 | 371 | 427 | 482 | 538 | 593 | 649
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 |  | 4 | [15 empty] | 5 | 6 | 7 | 8 | 9
1 | Carbon steel C <= 0.3% | 216495379220 | 212358524840 | 208221670460 | 203395340350 | 198569010240 | 195121631590 | 190984777210 | 188226874290 | 184090019910 | 175816311150 | 166853126660 | 154442563520 | 140653048920 | 124105631400 | 0 | 1 | Carbon steel C <= 0.3% | 31.4 | 30.8 | 30.2 | 29.5 | 28.8 | 28.3 | 27.7 | 27.3 | 26.7 | 25.5 | 24.2 | 22.4 | 20.4 | 18
2 | Carbon steel C => 0.3% | 215116427760 | 210979573380 | 206842719000 | 202016388890 | 197190058780 | 193742680130 | 189605825750 | 186847922830 | 182711068450 | 174437359690 | 165474175200 | 153063612060 | 139274097460 | 123416155670 | 106179262420 | 2 | Carbon steel C => 0.3% | 31.2 | 30.6 | 30 | 29.3 | 28.6 | 28.1 | 27.5 | 27.1 | 26.5 | 25.3 | 24 | 22.2 | 20.2 | 17.9 | 15.4
3 | Carbon-moly steels | 214426952030 | 210290097650 | 206153243270 | 201326913160 | 196500583050 | 193053204400 | 188916350020 | 186158447100 | 182021592720 | 174437359690 | 164784699470 | 153063612060 | 138584621730 | 122726679940 | 105489786690 | 3 | Carbon-moly steels | 31.1 | 30.5 | 29.9 | 29.2 | 28.5 | 28 | 27.4 | 27 | 26.4 | 25.3 | 23.9 | 22.2 | 20.1 | 17.8 | 15.3
4 | Nickel steels Ni 2% - 9% | 204084816080 | 200637437430 | 196500583050 | 191674252940 | 186847922830 | 184090019910 | 179953165530 | 177195262610 | 173747883960 | 169611029580 | 158579417900 | 0 | 0 | 0 | 0 | 4 | Nickel steels Ni 2% - 9% | 29.6 | 29.1 | 28.5 | 27.8 | 27.1 | 26.7 | 26.1 | 25.7 | 25.2 | 24.6 | 23
5 | Cr-Mo steels Cr 1/2% - 2% | 217874330680 | 213737476300 | 209600621920 | 204774291810 | 199947961700 | 196500583050 | 192363728670 | 189605825750 | 185468971370 | 181332116990 | 175816311150 | 170989981040 | 164784699470 | 158579417900 | 150305709140 | 5 | Cr-Mo steels Cr 1/2% - 2% | 31.6 | 31 | 30.4 | 29.7 | 29 | 28.5 | 27.9 | 27.5 | 26.9 | 26.3 | 25.5 | 24.8 | 23.9 | 23 | 21.8
6 | Cr-Mo steels Cr 2 1/4% - 3% | 224769087980 | 220632233600 | 216495379220 | 210979573380 | 205463767540 | 202705864620 | 198569010240 | 195121631590 | 190984777210 | 186847922830 | 181332116990 | 176505786880 | 169611029580 | 163405748010 | 155132039250 | 6 | Cr-Mo steels Cr 2 1/4% - 3% | 32.6 | 32 | 31.4 | 30.6 | 29.8 | 29.4 | 28.8 | 28.3 | 27.7 | 27.1 | 26.3 | 25.6 | 24.6 | 23.7 | 22.5
7 | Cr-Mo steels Cr 5% - 9% | 226837515170 | 222700660790 | 218563806410 | 213048000570 | 207532194730 | 204774291810 | 199947961700 | 197190058780 | 193053204400 | 188226874290 | 179953165530 | 170300505310 | 156510990710 | 140653048920 | 125484582860 | 7 | Cr-Mo steels Cr 5% - 9% | 32.9 | 32.3 | 31.7 | 30.9 | 30.1 | 29.7 | 29 | 28.6 | 28 | 27.3 | 26.1 | 24.7 | 22.7 | 20.4 | 18.2
8 | Chromium steels Cr 12%, 17%, 27% | 215116427760 | 211669049110 | 207532194730 | 201326913160 | 196500583050 | 192363728670 | 188226874290 | 184090019910 | 179953165530 | 176505786880 | 170300505310 | 159958369360 | 148237281950 | 131689864430 | 114452971180 | 8 | Chromium steels Cr 12%, 17%, 27% | 31.2 | 30.7 | 30.1 | 29.2 | 28.5 | 27.9 | 27.3 | 26.7 | 26.1 | 25.6 | 24.7 | 23.2 | 21.5 | 19.1 | 16.6
9 | Austenitic steels (TP304, 310, 316, 321, 347) | 208911146190 | 204774291810 | 200637437430 | 195121631590 | 190295301480 | 186158447100 | 182711068450 | 177884738340 | 174437359690 | 170989981040 | 166163650930 | 162026796550 | 157200466440 | 152374136330 | 146168854760 | 9 | Austenitic steels (TP304, 310, 316, 321, 347) | 30.3 | 29.7 | 29.1 | 28.3 | 27.6 | 27 | 26.5 | 25.8 | 25.3 | 24.8 | 24.1 | 23.5 | 22.8 | 22.1 | 21.2
| Cast iron | [16 empty] | Cast iron
| Gray cast iron |  |  |  | 13.4 | 13.2 | 12.9 | 12.6 | 12.2 | 11.7 | 11 | 10.2 | [5 empty] | Gray cast iron |  |  |  | 13.4 | 13.2 | 12.9 | 12.6 | 12.2 | 11.7 | 11 | 10.2
|  | Mpsi = | 6894757300 | Pa

## PVC_40 (hidden)
1 | 2 | 3 | 4 | 5 | 6
2 |  | PVC pipe material |  | CPVC 4120
3 |  | Dimensions according |  | ASTM D2846 / D2846M "Standard Specification for Chlorinated Poly(Vinyl Chloride) (CPVC)
4 |  | Pressure according |  | ASTM pressure equation
5
6 |  | Schedule 40 PVC Pipe |  | CPVC 4120
7 |  | Size | de | s | P
8 |  | in | mm | mm | bar
9 |  | 0.5 | 21.336 | 2.7686 | 41.1233
10 |  | 0.75 | 26.67 | 2.8702 | 33.2597
11 |  | 1 | 33.401 | 3.3782 | 31.0322
12 |  | 1.25 | 42.164 | 3.556 | 25.4017
13 |  | 1.5 | 48.26 | 3.683 | 22.7861
14 |  | 2 | 60.325 | 3.9116 | 19.1228
15 |  | 2.5 | 73.025 | 5.1562 | 20.9526
16 |  | 3 | 88.9 | 5.4864 | 18.1397
17 |  | 4 | 114.3 | 6.0198 | 15.3325
18 |  | 5 | 141.3002 | 6.5532 | 13.4126
19 |  | 6 | 168.275 | 7.112 | 12.1704
20 |  | 8 | 219.075 | 8.4328 | 11.0409
21 |  | 10 | 273.05 | 9.271 | 9.6932
22 |  | 12 | 323.85 | 10.3124 | 9.0709

## PVC_80 (hidden)
1 | 2 | 3 | 4 | 5 | 6
2 |  | PVC pipe material |  | CPVC 4120
3 |  | Dimensions according |  | ASTM D2846 / D2846M "Standard Specification for Chlorinated Poly(Vinyl Chloride) (CPVC)
4 |  | Pressure according |  | ASTM pressure equation
5
6 |  | Schedule 80 PVC Pipe |  | CPVC 4120
7 |  | Size | de | s | P
8 |  | in | mm | mm | bar
9 |  | 0.5 | 21.336 | 3.7338 | 58.501
10 |  | 0.75 | 26.67 | 3.9116 | 47.4015
11 |  | 1 | 33.401 | 4.5466 | 43.4564
12 |  | 1.25 | 42.164 | 4.8514 | 35.8584
13 |  | 1.5 | 48.26 | 5.08 | 32.4459
14 |  | 2 | 60.325 | 5.5372 | 27.8731
15 |  | 2.5 | 73.025 | 7.0104 | 29.2875
16 |  | 3 | 88.9 | 7.62 | 25.8553
17 |  | 4 | 114.3 | 8.5598 | 22.3256
18 |  | 5 | 141.3002 | 9.525 | 19.9347
19 |  | 6 | 168.275 | 10.9728 | 19.2381
20 |  | 8 | 219.075 | 12.7 | 16.9717
21 |  | 10 | 273.05 | 15.0622 | 16.1016
22 |  | 12 | 323.85 | 17.4498 | 15.7065